## About
BGCL BAU Generation Capacity Lifetime
Source: | All except nuclear and solar thermal
Directorate of Electricity Indonesia, Centre for Global Cooperation (Danish Energy Agency)
2021
Technology Data for the Indonesian Power Sector
https://ens.dk/sites/ens.dk/files/Globalcooperation/technology_data_for_the_indonesian_power_sector_-_final.pdf
Nuclear, solar thermal
National Renewable Energy Laboratory
2010
Cost and Performance Assumptions for Modeling Electricity Generation Technologies
http://www.nrel.gov/docs/fy11osti/48595.pdf
Page 157, Figure 113
Notes
This variable represents the lifetimes of different power plant types.
We adjust the data for Indonesia, except nuclear and solar thermal since both are not used in indonesia.
We consider the lifetime of petroleum (oil) - burning plants to be the same as crude oil, heavy oil.
We assume lignite plants have the same lifetime as hard coal plants.

## data - Indonesia
Geothermal | [9 empty] | Coal - ultra supercritical
Technology | Geothermal power plant - large system (flash or dry) | [8 empty] | Technology | Ultra-supercritical coal power plant
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data Lower Upper Lower Upper
Generating capacity for one unit (MWe) | 55 | 55 | 55 | 30 | 500 | 30 | 500 |  | 1 | Generating capacity for one unit (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
Generating capacity for total power plant (MWe) | 110 | 110 | 110 | 30 | 500 | 30 | 500 |  | 1 | Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
Electricity efficiency, net (%), name plate | 16 | 17 | 18 | 8 | 18 | 10 | 20 | A | 5 | Electricity efficiency, net (%), name plate | 43 | 44 | 45 | 40 | 45 | 42 | 47 |  | 1,3,6,7
Electricity efficiency, net (%), annual average | 15 | 16 | 17 | 8 | 18 | 10 | 20 | A | 5 | Electricity efficiency, net (%), annual average | 42 | 43 | 44 | 40 | 45 | 42 | 47 |  | 1,3
Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1 | Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1 | Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1 | Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 |  | 1 | Construction time (years) | 4 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 1 | Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants | [9 empty] | Additional data for non thermal plants
Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1 | Capacity factor (%), theoretical | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1 | Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations | [9 empty] | Ramping configuration
Ramping (% per minute) | 3 | 10 | 20 | [5 empty] | 8 | Ramping (% per minute) | 5 | 5 | 5 | 4 | 5 | 4 | 5 | B | 1
Minimum load (% of full load) | [9 empty] | Minimum load (% of full load) | 30 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
Warm start-up time (hours) | [9 empty] | Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
Cold start-up time (hours) | [9 empty] | Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment | [9 empty] | Environment
PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | C | 6 | PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | F | 2,4
SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | C | 6 | SO2 (degree of desulphuring, %) | 73 | 73 | 73 | 73 | 95 | 73 | 95 | C,D | 2,4
NOX (g per GJ fuel) | - | - | - | - | - | - | - | C | 6 | NOX (g per GJ fuel) | 263 | 263 | 263 | 263 | 263 | 263 | 263 | D | 2,4
CH4 (g per GJ fuel) | - | - | - | - | - | - | - | C | 6 | CH4 (g per GJ fuel) | - | - | - | - | - | - | -
N2O (g per GJ fuel) | - | - | - | - | - | - | - | C | 6 | N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data | [9 empty] | Financial data
Nominal investment (M$/MWe) | 4 | 3.44 | 2.84 | 2.7 | 5.75 | 1.7 | 4.55 | B,D,E,F | 1,2,3,4 | Nominal investment (M$/MWe) | 1.52 | 1.48 | 1.43 | 1.14 | 1.91 | 1.07 | 1.79 | E,G,H | 1,3,6,7
- of which equipment | 60% | 60% | 60% | 40% | 70% | 40% | 70% |  | 3 | - of which equipment
- of which installation | 40% | 40% | 40% | 30% | 50% | 30% | 50% |  | 3 | - of which installation
Fixed O&M ($/MWe/year) | 50000 | 43000 | 35500 | 37500 | 62500 | 26600 | 44400 | B,D | 1,4 | Fixed O&M ($/MWe/year) | 56600 | 54900 | 53200 | 42500 | 70800 | 39900 | 66500 | G | 1,3,6,7
Variable O&M ($/MWh) | 0.25 | 0.22 | 0.18 | 0.19 | 0.31 | 0.14 | 0.23 | B,D | 1,4 | Variable O&M ($/MWh) | 0.11 | 0.11 | 0.1 | 0.08 | 0.14 | 0.08 | 0.13 | G | 1,3
Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | - |  |  | Start-up costs ($/MWe/start-up) | 50 | 50 | 50 | 40 | 100 | 40 | 100 |  | 5
Technology specific data
Exploration costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
Confirmation costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
Hydropower | [9 empty] | Coal - supercritical
Technology | Hydro power plant - large system | [8 empty] | Technology | Supercritical coal power plant
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data Lower Upper Lower Upper
Generating capacity for one unit (MWe) | 150 | 150 | 150 | 100 | 2000 | 100 | 2000 |  | 1,8,10 | Generating capacity for one unit (MWe) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  | 1
Generating capacity for total power plant (MWe) | 150 | 150 | 150 | 100 | 2000 | 100 | 2000 |  | 1,8,10 | Generating capacity for total power plant (MWe) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  | 1
Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7 | Electricity efficiency, net (%), name plate | 38 | 39 | 40 | 33 | 40 | 35 | 42 |  | 1,3,6,7
Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7 | Electricity efficiency, net (%), annual average | 37 | 38 | 39 | 33 | 40 | 35 | 42 |  | 1,3
Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1 | Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1 | Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 | B | 1 | Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
Construction time (years) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1 | Construction time (years) | 4 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
Space requirement (1000 m2/MWe) | 62 | 62 | 62 | 47 | 78 | 47 | 78 | C | 1 | Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants | [9 empty] | Additional data for non thermal plants
Capacity factor (%), theoretical | 40 | 40 | 40 | 20 | 95 | 20 | 95 |  | 2,12 | Capacity factor (%), theoretical | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | 36 | 36 | 36 | 20 | 95 | 20 | 95 |  | 2,12 | Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations | [9 empty] | Ramping configuration
Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3 | Ramping (% per minute) | 4 | 4 | 4 | 3 | 4 | 3 | 4 | B | 1
Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | Minimum load (% of full load) | 30 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3 | Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3 | Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment | [9 empty] | Environment
PM 2.5 (gram per Nm3) | 0 | 0 | 0 | [6 empty] | PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | F | 2,4
SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [6 empty] | SO2 (degree of desulphuring, %) | 73 | 73 | 73 | 73 | 95 | 73 | 95 | C,D | 2,4
NOX (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | NOX (g per GJ fuel) | 263 | 263 | 263 | 263 | 263 | 263 | 263 | D | 2,4
CH4 (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | CH4 (g per GJ fuel) | - | - | - | - | - | - | -
N2O (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data | [9 empty] | Financial data
Nominal investment (M$/MWe) | 2.08 | 2 | 1.85 | 1.65 | 2.25 | 1.4 | 2.05 | D,E,F | 1,4,5,6,9 | Nominal investment (M$/MWe) | 1.4 | 1.36 | 1.32 | 1.05 | 1.75 | 0.99 | 1.65 | E,G,H | 1,3,6,7
- of which equipment | 30% | 30% | 30% | 20% | 50% | 20% | 50% |  | 11 | - of which equipment
- of which installation | 70% | 70% | 70% | 50% | 80% | 50% | 80% |  | 11 | - of which installation
Fixed O&M ($/MWe/year) | 37700 | 36200 | 33600 | 28300 | 47100 | 25200 | 42000 | C | 1,4,5,6 | Fixed O&M ($/MWe/year) | 41200 | 40000 | 38700 | 30900 | 51500 | 29000 | 48400 | G | 1,3,6,7
Variable O&M ($/MWh) | 0.65 | 0.62 | 0.58 | 0.49 | 0.81 | 0.43 | 0.72 | C | 1,5 | Variable O&M ($/MWh) | 0.12 | 0.12 | 0.11 | 0.09 | 0.15 | 0.08 | 0.14 | G | 1,3
Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | - |  |  | Start-up costs ($/MWe/start-up) | 50 | 50 | 50 | 40 | 100 | 40 | 100 |  | 5
Solar PV | [9 empty] | Coal - subcritical & lignite
Technology | Utility-scale Solar PV | [8 empty] | Technology | Subcritical coal power plant
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data Lower Upper Lower Upper | [9 empty] | Energy/technical data Lower Upper Lower Upper
Generating capacity a typical power plant (MWe) | 10 | 20 | 50 |  |  |  |  | C | 1 | Generating capacity for one unit (MWe) | 150 | 150 | 150 | 100 | 200 | 100 | 200 |  | 1
Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | A |  | Generating capacity for total power plant (MWe) | 150 | 150 | 150 | 100 | 200 | 100 | 200 |  | 1
Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | A |  | Electricity efficiency, net (%), name plate | 35 | 36 | 37 | 30 | 38 | 33 | 39 |  | 1,2,3
Forced outage (%) | - | - | - | [6 empty] | Electricity efficiency, net (%), annual average | 34 | 35 | 36 | 29 | 37 | 32 | 38 |  | 1,2,3
Planned outage (weeks per year) | - | - | - | [6 empty] | Forced outage (%) | 7 | 5 | 3 | 5 | 20 | 2 | 7 | A | 1
Technical lifetime (years) | 35 | 40 | 40 | 25 | 40 | 35 | 45 |  | 1,6 | Planned outage (weeks per year) | 6 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.25 | 1 |  | 1 | Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
Space requirement (1000 m2/MWp) | 14 | 14 | 14 | 13 | 18 | 13 | 18 |  | 6 | Construction time (years) | 3 | 3 | 3 | 2 | 4 | 2 | 4 |  | 1
Additional data for non thermal plants | [9 empty] | Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Capacity factor (%), theoretical | 19 | 22 | 22 | 17 | 23 | 17 | 23 |  | 1,2 | Additional data for non thermal plants
Capacity factor (%), incl. outages | 19 | 22 | 22 | 17 | 23 | 17 | 23 |  | 1,2 | Capacity factor (%), theoretical | - | - | - | - | - | - | -
Ramping configurations | [9 empty] | Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping (% per minute) | - | - | - | - | - | - | - | B |  | Ramping configuration
Minimum load (% of full load) | - | - | - | - | - | - | - | B |  | Ramping (% per minute) | 3.5 | 3.5 | 3.5 | 2 | 4 | 2 | 4 | B | 1
Warm start-up time (hours) | - | - | - | - | - | - | - | B |  | Minimum load (% of full load) | 30 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
Cold start-up time (hours) | - | - | - | - | - | - | - | B |  | Warm start-up time (hours) | 3 | 3 | 3 | 1 | 5 | 1 | 5 | B | 1
Environment | [9 empty] | Cold start-up time (hours) | 8 | 8 | 8 | 5 | 12 | 5 | 12 | B | 1
PM 2.5 (gram per Nm3) | 0 | 0 | 0 | [6 empty] | Environment
SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [6 empty] | PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | A,F | 2,4
NOX (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | SO2 (degree of desulphuring, %) | 73 | 80 | 95 | 73 | 95 | 73 | 95 | A,C,D | 2,4
CH4 (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | NOX (g per GJ fuel) | 263 | 150 | 38 | 263 | 263 | 263 | 263 | A,D | 2,4
N2O (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | CH4 (g per GJ fuel)
Financial data | [9 empty] | N2O (g per GJ fuel)
Nominal investment (M$/MWe) | 0.79 | 0.56 | 0.41 | 0.7 | 1.2 | 0.31 | 0.71 | D,R,S | 1,3,4 | Financial data
- of which equipment | 44% | 39% | 35% | [6 empty] | Nominal investment (M$/MWe) | 1.65 | 1.6 | 1.55 | 1 | 1.7 | 1.05 | 1.7 | E,H | 1,3
- of which installation | 56% | 61% | 65% | [6 empty] | - of which equipment
Fixed O&M ($/MWe/year) | 14400 | 10000 | 8000 | 10800 | 18000 | 5300 | 10700 | E,Q | 5,6 | - of which installation
Variable O&M ($/MWh) | 0 | 0 | 0 | [6 empty] | Fixed O&M ($/MWe/year) | 45300 | 43900 | 42600 | 34000 | 56600 | 32000 | 53300 | G | 1,3
Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | [6 empty] | Variable O&M ($/MWh) | 0.13 | 0.12 | 0.12 | 0.09 | 0.16 | 0.09 | 0.15 | G | 1,3
Technology specific data | [9 empty] | Start-up costs ($/MWe/start-up) | 110 | 110 | 110 | 50 | 200 | 50 | 200 |  | 5
Global horizontal irradiance (kWh/m2/y) | 1800 | 1800 | 1800 |  |  |  |  | F | 8
DC/AC sizing factor (Wp/W) | 1.1 | 1.1 | 1.1 |  |  |  |  | G
Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 8
Performance ratio [-] | 0.86 | 0.95 | 0.97 |  |  |  |  | I | 6
PV module conversion efficiency (%) | 20.5% | 23% | 26% | [5 empty] | 6
Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
Full load hours (kWh/kW) | 1700 | 1950 | 1950 |  |  |  |  | J, L
Peak power full load hours (kWh/kWp) | 1550 | 1750 | 1750 |  |  |  |  | K, L
Financial data
PV module & inverter cost ($/Wp) | 0.32 | 0.2 | 0.13 | [5 empty] | 7
Balance Of Plant cost ($/Wp) | 0.4 | 0.31 | 0.24 | [5 empty] | 7
Specific investment, total system ($/Wp) | 0.72 | 0.51 | 0.37 |  |  |  |  | M | 5,6,9
Specific investment, total system (M$/MW) | 0.79 | 0.56 | 0.41 |  |  |  |  | P
Wind - onshore | [9 empty] | Natural gas non peaker
Technology | Wind power - Onshore | [8 empty] | Technology | Simple Cycle Gas Turbine - large system
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MWe) | 3.5 | 4 | 5 | [5 empty] | 3 | Generating capacity for one unit (MWe) | 50 | 50 | 50 | 35 | 65 | 35 | 65 |  | 3
Generating capacity for total power plant (MWe) | 70 | 80 | 100 | [5 empty] | 1 | Generating capacity for total power plant (MWe) | 100 | 100 | 100 | 35 | 150 | 35 | 150 |  | 3
Electricity efficiency, net (%), name plate | 100 | 100 | 100 |  |  |  |  | A |  | Electricity efficiency, net (%), name plate | 34 | 36 | 40 | [5 empty] | 1,2
Electricity efficiency, net (%), annual average | 100 | 100 | 100 | [6 empty] | Electricity efficiency, net (%), annual average | 33 | 35 | 39 | [5 empty] | 1,2
Forced outage (%) | 2.5% | 2% | 2% | [6 empty] | Forced outage (%) | 2 | 2 | 2
Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 |  | 3 | Planned outage (weeks per year) | 3 | 3 | 3
Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 3 | Technical lifetime (years) | 25 | 25 | 25
Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 1 | Construction time (years) | 1.5 | 1.5 | 1.5 | 1.1 | 1.9 | 1.1 | 1.9 | B | 3
Space requirement (1000 m2/MWe) | 14 | 14 | 14 | [5 empty] | 1 | Space requirement (1000 m2/MWe) | 0.02 | 0.02 | 0.02 | 0.015 | 0.025 | 0.015 | 0.025 | B | 3
Additional data for non thermal plants | [9 empty] | Additional data for non thermal plants
Capacity factor (%), theoretical | 35 | 36 | 37 | 20 | 45 | 20 | 45 | B |  | Capacity factor (%), theoretical | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | 34 | 35 | 36 | [6 empty] | Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations | [9 empty] | Ramping configurations
Ramping (% per minute) | - | - | - |  |  |  |  | F |  | Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 3,8
Minimum load (% of full load) | - | - | - |  |  |  |  | F |  | Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 | A | 6
Warm start-up time (hours) | - | - | - | [6 empty] | Warm start-up time (hours) | 0.25 | 0.23 | 0.2 | [5 empty] | 3
Cold start-up time (hours) | - | - | - | [6 empty] | Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment | [9 empty] | Environment
PM 2.5 (gram per Nm3) | 0 | 0 | 0 | [6 empty] | PM 2.5 (mg per Nm3) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 7
SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [6 empty] | SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
NOX (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | NOX (g per GJ fuel) | 86 | 60 | 20 | 20 | 86 | 20 | 86 | A,D | 3,7
CH4 (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | CH4 (g per GJ fuel) | - | - | - | - | - | - | -
N2O (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data | [9 empty] | Financial data
Nominal investment (M$/MWe) | 1.5 | 1.28 | 1.08 | 1.2 | 2.35 | 0.8 | 1.85 | D,G | 1 | Nominal investment (M$/MWe) | 0.77 | 0.73 | 0.68 | 0.65 | 1.2 | 0.55 | 1.1 | F,G,H | 1-5
- of which equipment | 65% | 65% | 65% |  |  |  |  | C | 2, 3 | - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
- of which installation | 35% | 35% | 35% |  |  |  |  | C | 2, 3 | - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
Fixed O&M ($/MWe/year) | 60000 | 51000 | 43200 | 30000 | 70000 | 25000 | 60000 |  | 4 | Fixed O&M ($/MWe/year) | 23200 | 22500 | 21800 | 17400 | 29000 | 16400 | 27300 | B | 1-5
Variable O&M ($/MWh) | 0 | 0 | 0 | [5 empty] | 4 | Variable O&M ($/MWh)
Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | [6 empty] | Start-up costs ($/MWe/start-up) | 24 | 24 | 24 | 18 | 30 | 18 | 30 | B | 6
Wind - offshore | [9 empty] | MSW
Technology | Wind power - Offshore | [8 empty] | Technology | Incineration Power Plant - Municipal Solid Waste
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MWe) | 8 | 10 | 12 | [5 empty] | 3 | Generating capacity for one unit (MWe) | 22 | 22 | 23
Generating capacity for total power plant (MWe) | 240 | 300 | 360 | [6 empty] | Generating capacity for total power plant (MWe) | 22 | 22 | 23
Electricity efficiency, net (%), name plate | 100 | 100 | 100 |  |  |  |  | A |  | Electricity efficiency, net (%), name plate | 29% | 30% | 31% | 28% | 32% | 30% | 33% | A | 1
Electricity efficiency, net (%), annual average | 100 | 100 | 100 |  |  |  |  | A |  | Electricity efficiency, net (%), annual average | 28% | 29% | 29% | 26% | 30% | 28% | 31% |  | 1
Forced outage (%) | 4% | 3% | 3% | [5 empty] | 3 | Forced outage (%) | 1% | 1% | 1% | [5 empty] | 1
Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | [5 empty] | 3 | Planned outage (weeks per year) | 2.9 | 2.6 | 2.1 | [5 empty] | 1
Technical lifetime (years) | 27 | 30 | 30 | 20 | 35 | 20 | 35 |  | 3 | Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 1
Construction time (years) | 3 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 3 | Construction time (years) | 2.5 | 2.5 | 2.5 | [5 empty] | 1
Space requirement (1000 m2/MWe) | 185 | 185 | 185 | 168 | 204 | 168 | 204 |  | 3 | Space requirement (1000 m2/MWe) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
Additional data for non thermal plants | [9 empty] | Additional data for non thermal plants
Capacity factor (%), theoretical | 50 | 51 | 52 | 20 | 45 | 20 | 45 | B | 2 | Capacity factor (%), theoretical | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | 47.9 | 49.1 | 50.7 | [6 empty] | Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations | [9 empty] | Ramping configurations
Ramping (% per minute) | - | - | - |  |  |  |  | F |  | Ramping (% per minute) | 10 | 10 | 10 | 7.5 | 12.5 | 7.5 | 12.5 | C | 1
Minimum load (% of full load) | - | - | - |  |  |  |  | F |  | Minimum load (% of full load) | 20 | 20 | 20 | 15 | 25 | 15 | 25 | C | 1
Warm start-up time (hours) | - | - | - | [6 empty] | Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.4 | 0.6 | C | 1
Cold start-up time (hours) | - | - | - | [6 empty] | Cold start-up time (hours) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | C | 1
Environment | [9 empty] | Environment
PM 2.5 (gram per Nm3) | 0 | 0 | 0 | [6 empty] | PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [6 empty] | SO2 (degree of desulphuring, %)
NOX (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | NOX (g per GJ fuel)
CH4 (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | CH4 (g per GJ fuel)
N2O (g per GJ fuel) | 0 | 0 | 0 | [6 empty] | N2O (g per GJ fuel)
Financial data | [9 empty] | Financial data
Nominal investment (M$/MWe) | 3.5 | 2.98 | 2.52 | 2.4 | 3.7 | 1.55 | 2.9 | D,G | 3 | Nominal investment ( million $/MWe) | 6.8 | 6.3 | 5.6 | 5.1 | 7 | 4.2 | 7 | C | 1
- of which equipment | 45% | 45% | 45% |  |  |  |  | C | 3 | - of which equipment | 4 | 3.4 | 2.8 | 3 | 3.5 | 2.1 | 3.5 |  | 1
- of which installation | 55% | 55% | 55% |  |  |  |  | C | 3 | - of which installation | 2.8 | 2.9 | 2.8 | 2.1 | 3.5 | 2.1 | 3.5 |  | 1
Fixed O&M ($/MWe/year) | 72600 | 61700 | 52300 | 58200 | 78200 | 38000 | 57200 |  | 4 | Fixed O&M ($/MWe/year) | 243700 | 224800 | 193500 | 195000 | 304600 | 154800 | 241900 | C | 1
Variable O&M ($/MWh) | 5.5 | 4.8 | 3.9 | 3.4 | 5.8 | 2.7 | 4.3 |  | 4 | Variable O&M ($/MWh) | 24.1 | 23.4 | 22.6 | 18.1 | 30.2 | 16.9 | 28.2 | C | 1
Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | [6 empty] | Start-up costs ($/MWe/start-up)
Technology specific data
[10 empty] | Waste treatment capacity (tonnes/h) | 27.7 | 27.7 | 27.7 |  |  |  |  | B
Biomass | [9 empty] | Natural gas - peaker
Technology | Biomass power plant (smal plant - palm oil / rice husk ) | [8 empty] | Technology | Combined Cycle Gas Turbine
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5 | Generating capacity for one unit (MWe) | 600 | 600 | 600 | 200 | 800 | 200 | 800 |  | 1
Generating capacity for total power plant (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5 | Generating capacity for total power plant (MWe) | 600 | 600 | 600 | 200 | 800 | 200 | 800 |  | 1
Electricity efficiency, net (%), name plate | 32 | 32 | 32 | 25 | 35 | 25 | 35 |  | 1,3,7 | Electricity efficiency, net (%), name plate | 57 | 60 | 61 | 45 | 62 | 55 | 65 |  | 1,3,5,10
Electricity efficiency, net (%), annual average | 31 | 31 | 31 | 25 | 35 | 25 | 35 |  | 1,3,7 | Electricity efficiency, net (%), annual average | 56 | 59 | 60 | 39 | 61 | 54 | 64
Forced outage (%) | 7 | 7 | 7 | 5 | 9 | 5 | 9 | A | 1 | Forced outage (%) | 5 | 5 | 5 | 3 | 10 | 3 | 10 |  | 1
Planned outage (weeks per year) | 6 | 6 | 6 | 5 | 8 | 5 | 8 | A | 1 | Planned outage (weeks per year) | 5 | 5 | 5 | 3 | 8 | 3 | 8 |  | 1
Technical lifetime (years) | 25 | 25 | 25 | 19 | 31 | 19 | 31 | A | 8,10 | Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 1
Construction time (years) | 2 | 2 | 2 | 2 | 3 | 2 | 3 | A | 10 | Construction time (years) | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
Space requirement (1000 m2/MWe) | 35 | 35 | 35 | 26 | 44 | 26 | 44 | A | 1,9 | Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants | [9 empty] | Additional data for non thermal plants
Capacity factor (%), theoretical | - | - | - | - | - | - | - |  |  | Capacity factor (%), theoretical | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | - | - | - | - | - | - | - |  |  | Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations | [9 empty] | Ramping configurations
Ramping (% per minute) | 10 | 10 | 10 | [5 empty] | 3 | Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 1,2
Minimum load (% of full load) | 30 | 30 | 30 | [5 empty] | 3 | Minimum load (% of full load) | 45 | 30 | 15 | 30 | 50 | 10 | 40 | A | 5
Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3 | Warm start-up time (hours) | 2 | 1 | 1 | 1 | 3 | 0.5 | 2 | A | 1,5
Cold start-up time (hours) | 10 | 10 | 10 | [5 empty] | 3 | Cold start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 |  | 1,5
Environment | [9 empty] | Environment
PM 2.5 (mg per Nm3) | 12.5 | 12.5 | 12.5 | [5 empty] | 3 | PM 2.5 (mg per Nm3) | 30 | 30 | 30
SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 3 | SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 3 | NOX (g per GJ fuel) | 86 | 60 | 20 | 20 | 86 | 20 | 86 | A,D | 7,8
CH4 (g per GJ fuel) | 0.9 | 0.9 | 0.9 | [5 empty] | 3 | CH4 (g per GJ fuel) | - | - | - | - | - | - | -
N2O (g per GJ fuel) | 1.1 | 1.1 | 1.1 | [5 empty] | 3 | N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data | [9 empty] | Financial data
Nominal investment (M$/MWe) | 2 | 1.82 | 1.6 | 1.3 | 2.25 | 1.2 | 2 | B,C | 4-8,11 | Nominal investment (M$/MWe) | 0.69 | 0.66 | 0.61 | 0.65 | 1 | 0.55 | 0.9 | F,H | 1,3,10
- of which equipment | 65 | 65 | 65 | 50 | 85 | 50 | 85 |  | 1,2 | - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
- of which installation | 35 | 35 | 35 | 15 | 50 | 15 | 50 |  | 1,2 | - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
Fixed O&M ($/MWe/year) | 47600 | 43800 | 38100 | 35700 | 59500 | 28600 | 47600 | A | 4,5,8,11 | Fixed O&M ($/MWe/year) | 23500 | 22800 | 22100 | 17600 | 29400 | 16600 | 27600 | B | 1,3
Variable O&M ($/MWh) | 3 | 2.8 | 2.4 | 2.3 | 3.8 | 1.8 | 3 | A | 5,11 | Variable O&M ($/MWh) | 2.3 | 2.23 | 2.16 | 1.73 | 2.88 | 1.62 | 2.7 | B | 1
Start-up costs ($/MWe/start-up) | [9 empty] | Start-up costs ($/MWe/start-up) | 80 | 80 | 80 | 60 | 100 | 60 | 100 | B | 6
Heavy or residual fuel oil, petroleum, crude oil
Technology | Diesel engine (using fuel oil)
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data Lower Upper Lower Upper
Generating capacity for one unit (MWe) | 20 | 20 | 20 | [5 empty] | 1
Generating capacity for total power plant (MWe) | 100 | 100 | 100
Electricity efficiency, net (%), name plate | 46 | 47 | 48 | [5 empty] | 1
Electricity efficiency, net (%), annual average | 45 | 46 | 47 | 43 | 47 | 45 | 52 |  | 1
Forced outage (%) | 3 | 3 | 3
Planned outage (weeks per year) | 1 | 1 | 1 | [5 empty] | 2
Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 2
Construction time (years) | 1 | 1 | 1 | [5 empty] | 2
Space requirement (1000 m2/MWe) | 0.05 | 0.05 | 0.05 | [5 empty] | 2
Additional data for non thermal plants
Capacity factor (%), theoretical | - | - | -
Capacity factor (%), incl. outages | - | - | -
Ramping configurations
Ramping (% per minute) | 25 | 25 | 25
Minimum load (% of full load) | 6 | 6 | 6 |  |  |  |  | A | 1
Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | [5 empty] | 1
Cold start-up time (hours) | 0.3 | 0.3 | 0.3
Environment
PM 2.5 (gram per Nm3) | 20 | 20 | 20 |  |  |  |  | B, C | 3.4
SO2 (degree of desulphuring, %) | 0 | 0 | 0 |  |  |  |  | C | 3,4
SO2 (g per GJ fuel) | 224 | 224 | 224 |  |  |  |  | C | 3.4
NOX (g per GJ fuel) | 280 | 280 | 280 |  |  |  |  | C | 3.4
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M$/MWe) | 0.8 | 0.8 | 0.78 | 0.7 | 0.9 | 0.65 | 0.85 | D | 6.7
- of which equipment
- of which installation
Fixed O&M ($/MWe/year) | 8000 | 8,000 | 7,760 | [5 empty] | 2
Variable O&M ($/MWh) | 6.4 | 6 | 5.8 | [5 empty] | 2
Start-up costs ($/MWe/start-up) | - | - | -

## NREL Plant Lifetimes
Plant Type | Lifetime (yr)
Coal | 45
IGCC | 45
Combustion Turbine | 45
Combined Cycle | 45
Nuclear | 60
Biomass | 45
Geothermal | 30
Wind (onshore) | 30
Solar Thermal | 30
Solar PV | 30

## BGCL
Electricity Source | Lifetime (years)
hard coal | 30
natural gas nonpeaker | 25
nuclear | 60
hydro | 50
onshore wind | 27
solar PV | 35
solar thermal | 30
biomass | 25
geothermal | 30
petroleum | 25
natural gas peaker | 25
lignite | 30
offshore wind | 27
crude oil | 25
heavy or residual fuel oil | 25
municipal solid waste | 25